Handouk

►FEATURES

- Designed for high inrush current load

- Application

Air-conditioner, refrigerator, compressor etc.

►CONTACT  DATA

| Contact Form | 1 Form A | 2 Form A |
| --- | --- | --- |
| Initial Contact Resistance | Max: 50mΩ |
| Contact Material | Silver Alloy |
| Rated Load | Resistive | 30A 277VAC | 25A 277VAC |
|  | Motor | 1.5HP,120VAC 3HP,240VAC |
| Max. Switching Current | 50A |
| Max. Switching Power | 8,310VA | 6,925VA |
| Mechanical life | 5ⅹ106 OPS (18,000ops/h) |
| Electrical life | 1ⅹ105 OPS (1,800ops/h) |

►CHARACTERISTICS

| Insulation Resistance | 100MΩ (500VDC) |
| --- | --- |
| Dielectric Strength between | Contact and contact | 2,000VAC/1min (Leakage current 1mA ) |
|  | Contact poles | 2,000VAC/1min (Leakage current 1mA ) |
|  | Contacts and coil | 4,000VAC/1min (Leakage current 1mA ) |
| Pick-up voltage(at 23℃) | AC,DC ≤ 75% rated voltage |
| Drop-out voltage(at 23℃) | AC,DC > 15% rated voltage |
| Operate time | ≤30ms |
| Release Time | ≤30ms |
| Max. allowable voltage(at 23℃) | 110% rated voltage |
| Atmospheric Pressure | 86 ~ 106KPa |
| Ambient temperature | 25℃ - 55℃ |
| Humidity | 35% to 85% RH |
| Shock resistance | Functional | 98m/s2 (10g) |
|  | Destructive | 980m/s2(100g) |
| Vibration resistance | 10 to 55HZ Dual amplitude : 1.5mm |
| Install model | Plug-in terminal, Bolt Terminal, PCB terminal, Din rail terminal |
| Unit weight | Plug-in terminal : Approx. 90g Bolt type : Approx. 120g |

►Coil DATA

| Nominal coil power | 2.5VA(AC), 1.9W(DC) |
| --- | --- |
| Nominal Voltage | 6~400VAC, 6~220VDC |

| Nominal Voltage (VDC) | Pick-up Voltage (≤) VDC | Drop-out Voltage (≤) VDC | Coil Resistance at 25℃ Ω ± 10% |
| --- | --- | --- | --- |
| 6 | 4.5 | 0.9 | 18.9 |
| 12 | 9 | 1.8 | 75 |
| 24 | 18 | 3.6 | 303 |
| 48 | 27 | 7.2 | 1,220 |
| 100 | 36 | 15 | 5,260 |
| 110 | 82.5 | 16.5 | 6,360 |
| 220 | 165 | 33 | 25,474 |
| Nominal Voltage (VAC) | Pick-up Voltage (≤) VAC | Drop-out Voltage (≤) VAC | Coil Resistance at 25℃ Ω ± 10% |
| 6 | 4.5 | 0.9 | 17 |
| 12 | 9 | 1.8 | 65 |
| 24 | 18 | 3.6 | 275 |
| 48 | 27 | 7.2 | 1,100 |
| 100/120 | 75/90 | 15/18 | 5,200 |
| 200/240 | 150/180 | 30/36 | 21,000 |
| 380/400 | 285/300 | 57/60 | 62,650 |

►ORDERING INFORMATION

►OUTLINE DIMENSIONS  (Unit: MM)

►OUTLINE DIMENSIONS  (UNIT: MM)

►OUTLINE DIMENSIONS  (UNIT: MM)

Disclaimer

This datasheet is for the customers’ reference. All the specifications are subject to change without notice.

# Text boxes

#### GH