HANDOUK

►FEATURES

● 5A, 10A Switching capabilities,

● SPST configurations,

● Subminiature, PCB layout

● Sealed and Unsealed types available

►CONTACT DATA

| Contact Form | 1A(SPST) |
| --- | --- |
| Contact Material | AgSnO2 |
| Rated load (Res. Load) | 5A 250VAC / 30VDC, 10A 125VAC |
| Initial Contact Resistance | 100mΩ Max at 24VDC 1A |
| Max. switching Voltage | 250VAC |
| Max. switching current | 5A |
| Max. switching power | 1,250VAC / 150W |
| UL/CUR rating | 12A 125VAC Res. 10A 277VAC/30VDC TV-5 1/4HP 125VAC / 250VAC |
| Life Expectancy | Electrical | 100,000 Operations (at 30 Operations / minute) |
|  | Mechanical | 10,000,000 Operations |

►OPERATION CONDITION

| Initial Insulation resistance | 100M ohm 500VDC |
| --- | --- |
| Dielectric strength Between | Coil and contacts | 2,500Vac, 1min. |
|  | Open contacts | 1,000Vac, 1min. |
| Operate time (at nominal voltage) | Max. 8ms |
| Release time (at nominal voltage) | Max. 5ms |
| Shock resistance | Functional | 100m/s2 |
|  | Destructive | 1,000m/s2 |
| Vibration resistance | 1.5 mm, 10 to 55Hz |
| Ambient temperature | -40°C~+70°C |
| Humidity | 35 % to 95% R.H. |
| Termination | PCB |
| Unit weight | Approx. 6g |
| Construction | Sealed & Unsealed |

►COIL Data

| Norminal Voltage (VDC) | Pick-up voltage VDC (Max.) | Drop-out voltag VDC (Min.) | Coil resistance Ω (10%) | allowable Voltage VDC(Max.) |
| --- | --- | --- | --- | --- |
| 3 | 2.25 | 0.15 | 20 | 3.90 |
| 5 | 3.75 | 0.25 | 55 | 6.50 |
| 6 | 4.50 | 0.30 | 80 | 7.80 |
| 9 | 6.75 | 0.45 | 180 | 11.70 |
| 12 | 9.00 | 0.60 | 320 | 15.60 |
| 18 | 13.50 | 0.90 | 720 | 23.40 |
| 24 | 18.00 | 1.20 | 1,280 | 31.20 |

►ORDERING INFORMATION

►DIMENSIONS  (Unit: mm)

►CHARACTERISTICS CURVE

# Text boxes

#### HC1