Handouk

►FEATURE

● 50A(GEG), 80A(GE80) switching capabilities

● Applicable to solar photovoltaic inverter

● 4KV dielectric strength coil to contacts

● 3mm contact gap (compliant to European Photovoltaic Standard)

● Class F UL insulation

►CONTACT DATA

| Contact Arrangement | GE80-1A (SPST) | GEG*-1A,2A (SPST, DPST) |
| --- | --- | --- |
| Initial Contact Resistance | 100mΩ(10A 13.5VDC) |
| Contact Material | AgSnO2, AgNi |
| Contact Ratings | 80A 60VDC / 80A 250VAC | 50A 277VAC |
| Max Switching Voltage | 277VAC/60VDC | 277VAC |
| Max Switching Current | 90A | 55A |
| Max Switching Power | 24,930VA | 15,235VA |
| Max Load Current | 100A 15min at room temp. |  |
| Electrical Life Expectancy | 6 x 103 Operations (80A 250VAC, at 85 , 1s on 9s off) 6 x 103Operations (80A 60VDC, at 85 , 1s on 9s off) | 3 x 104Operations (50A 277VAC, at room temp, 1s on 9s off) |
| Mechanical Life Expectancy | 1,000,000 Operations |

Notes: 1) The data shown above are initial values.

►OPERATION CONDITION

| Div | GE80-1A | GEG*-1A,2A |
| --- | --- | --- |
| Insulation Resistance | 1000MΩMin at 500VDC |
| Dielectric Strength Between | Open Contacts | 2,000Vrms 1min. |
|  | Contacts and coil | 4,000Vrms 1min. |
|  | Between contact sets | - | 2,000Vrms 1min. |
| Surge Voltage | 6kV (1.2/50µs) |
| Operate Time | 30ms |
| Release Time | 30ms |
| Ambient temperature | -40℃to+85℃ |
| Shock Resistance | Operating Extremes | 98m/s2 |
|  | Damage Limits | 980m/s2 |
| Vibration Resistance* | 1.5mm DA,10 to 55Hz |
| Humidity | 5% to 85% RH |
| Weight | Approx. 120g. | Approx. 90g. |
| Construction | Dust Protected | G1:Dust protected, G2/G3: Flux proofed |
| UL File | E222977 |
| Termination2) | PCB |

Notes: 1) The data shown above are initial values.

2) It does not allow using quick-connect terminations.

3) * ndex is not in relay width direction.

►ORDERING INFORMATION

►COIL PARAMETER

| Coil Power | Approx. 3.2W |
| --- | --- |
| Holding voltage | 60%~120% Un (at 23℃) 70%~95% Un (at 85℃) |

Notes: 1) The coil holding voltage is the voltage applied to coil 200ms after the rated voltage.

2) To avoid overheating and burning, the coil cannot be consistently

applied to with voltage larger than maximum holding voltage.

VDC                                                                                          (at 23℃)

| Nominal Voltage VDC | Pick-up Voltage VDC max 1) | Drop-out Voltage VDC min1) | Max. Voltage VDC *2) | Coil Resistance Ω |
| --- | --- | --- | --- | --- |
| 3 | 2.25 | 0.3 | 3.3 | 2.8±10% |
| 6 | 4.50 | 0.6 | 6.6 | 11.3±10% |
| 9 | 6.75 | 0.9 | 9.9 | 25±10% |
| 12 | 9.00 | 1.2 | 13.2 | 45±10% |
| 24 | 18.0 | 2.4 | 26.4 | 180±10% |
| 48 | 36.0 | 4.8 | 52.8 | 720±10% |

Notes: 1) The data shown above are initial values.

2) *Maximum voltage refers to the maximum voltage which relay coil could endure

in a short period of time

► safety approval  rating

| GEG1, GEG2, GEG3 | GE80 |
| --- | --- |
| AgSnO2 50A 277VAC | AgSnO2 80A 277VAC 80A 60VDC |

Notes: 1) All values unspecified are room temperature. 2) Only typical loads are listed obove. Other load specifications can be available upon request.

►DEMENSIONS(mm)

Remarks: 1) In case of no tolerance shown in outline dimension ≤1mm, tolerance should be ±0.2mm; outline dimension >1mm and  ≤ 5mm, tolerance should be ±0.3mm; outline dimension >5mm and  ≤5mm, tolerance should be ±0.4mm. 2) The tolerance without indicating for PCB layout is always  ±0.1mm.

Declaimer

The specification is for reference only. See to “Terminology and Guidelines” for more information. Specifications subject to change without notice. We could not evaluate all the performance and all the parameters for every possible application. Thus the user should be in a right position to choose the suitable product for their own application. If there is any quiry, please contact HANDOUK for the technical service. However, it is the user’s responsibility to determine which product should be used only.   HANDOUL Electronics Co., Ltd.  All right of HANDOUK are reserved.

# Text boxes

#### GEG/GE80