HANDOUK

■ FEATURES

●12A or 16A switching capability

● 1.5mm, 2.0mm contact gap available

● Sockets available

● Plastic sealed and flux proofed types available

● Class F & Class B insulation system

● Environmental friendly product (RoHS compliant)

● Outline Dimensions: (29.0ⅹ12.7ⅹ26)mm

| Contact data |
| --- |
| Contact arrangement | 2A/2B/2C |
| Contact resistance | 100mΩ max. (at 1A 6VDC) |
| Contact material | Ag alloy |
| Contact rating | HL42 types: NO/NC: 12A 250VAC HL42K types: NO/NC: 16A 250VAC |
| Max. switching voltage | 277VAC / 24VDC |
| Max. switching current | 16A |
| Max. switching power | 4000VA/ 380W |
| Min. switching load | 100mA 5VDC |
| Mechanical endurance | Normal contact type: 5,000,000 cycles min. 1.5mm and 2.0mm type: 1,000,000 cycles min. |
| Electrical endurance | HL42 type: (at ON/OFF=1s/9s, normal temp.) NO：12A 250VAC, R-load, 30,000cycles min. NC：12A 250VAC, R-load, 10,000cycles min. HL42K type: (at ON/OFF=1s/9s, normal temp.) NO：16A 250VAC, R-load, 30,000cycles min. NC：16A 250VAC, R-load, 10,000cycles min. |

| Characteristics (initial) |
| --- |
| Insulation resistance | 1000MΩ(at 500VDC) |
| Dielectric strength | Between coil and contacts: 5000V for 1 minute |
|  | Between open contacts: 3000V for 1 minute |
|  | Normal contact type: Between contact sets: 1000V for 1 minute 1.5mm contact type: Between contact sets: 2000V for 1 minute 2.0mm contact type: Between contact sets: 2500V for 1 minute |
| Operate time (at normal voltage) | 20ms max. |
| Release time (at normal voltage) | 20ms max. |
| vibration resistance | 10Hz-55Hz, at double amplitude 1.5mm |
| Shock resistance | Functional: Min. 100m/s2 Destructive: Min. 1000m/s2 |
| Ambient temperature | -40℃ to 85℃ |
| Humidity | 5% to 85% RH |
| Termination | PCB type. |
| Unit weight | Approx. 18g |
| Construction | Flux protected or washing type |

| Coil data (DC spec:0.2W) |
| --- |
| Rated voltage | Coil resistance (Ω) (at 23℃) | Operate voltage (at 23℃) | release voltage (at 23℃) | Allowable voltage range (at 23℃) | Nominal coil power (approx. W) |
|  |  | % of rated voltage |  |
| 003 | 45×(1±10%) | 80% max. | 5%min. | 95%-150% | 0.2 |
| 005 | 125×(1±10%) |  |  |  | 0.2 |
| 006 | 180×(1±10%) |  |  |  | 0.2 |
| 009 | 405×(1±10%) |  |  |  | 0.2 |
| 012 | 720×(1±10%) |  |  |  | 0.2 |
| 015 | 1125×(1±10%) |  |  |  | 0.2 |
| 018 | 1620×(1±10%) |  |  |  | 0.2 |
| 024 | 2880×(1±10%) |  |  |  | 0.2 |
| 036 | 6480×(1±10%) |  |  |  | 0.2 |
| 048 | 11520×(1±10%) |  |  |  | 0.2 |
| 060 | 16500×(1±10%) |  |  |  | 0.2 |
| 100 | 43000×(1±10%) |  |  |  | 0.2 |

| Coil data (DC spec: 0.53W) |
| --- |
| Rated voltage | Coil resistance (Ω) (at 23℃) | Operate voltage (at 23℃) | release voltage (at 23℃) | Allowable voltage range (at 23℃) | Nominal coil power (approx. W) |
|  |  | % of rated voltage |  |
| 003 | 17×(1±10%) | 75% max. | 5%min. | 95%-120% | 0.53 |
| 005 | 45×(1±10%) |  |  |  | 0.53 |
| 006 | 67×(1±10%) |  |  |  | 0.53 |
| 009 | 150×(1±10%) |  |  |  | 0.53 |
| 012 | 270×(1±10%) |  |  |  | 0.53 |
| 015 | 420×(1±10%) |  |  |  | 0.53 |
| 018 | 610×(1±10%) |  |  |  | 0.53 |
| 024 | 1086×(1±10%) |  |  |  | 0.53 |
| 036 | 2445×(1±10%) |  |  |  | 0.53 |
| 048 | 4347×(1±10%) |  |  |  | 0.53 |
| 060 | 6720×(1±10%) |  |  |  | 0.53 |
| 110 | 22830×(1±10%) |  |  |  | 0.53 |

| Coil data (normal contact gap: AC spec) |
| --- |
| Rated voltage | Coil resistance (Ω) (at 23℃) | Operate voltage (at23℃) | release voltage (at 23℃) | Allowable voltage range (at 23℃) | Nominal coil power (approx. VA) |
|  |  | % of rated voltage |  |
| 6 | 19×(1±10%) | 80% max. | 20%min. | 95%-120% | 1.1 |
| 12 | 72×(1±10%) |  |  |  | 1.1 |
| 24 | 290×(1±10%) |  |  |  | 1.1 |
| 48 | 1280×(1±10%) |  |  |  | 1.1 |
| 60 | 2100×(1±10%) |  |  |  | 1.1 |
| 110 | 6000×(1±10%) |  |  |  | 1.1 |
| 120 | 6000×(1±10%) |  |  |  | 1.1 |
| 110/120 | 6000×(1±10%) |  |  |  | 1.1 |
| 220 | 23000×(1±10%) |  |  |  | 1.1 |
| 230 | 23000×(1±10%) |  |  |  | 1.3 |
| 240 | 23000×(1±10%) |  |  |  | 1.3 |
| 220/240 | 23000×(1±10%) |  |  |  | 1.3 |

| Coil data (DC spec:0.8W) |
| --- |
| Rated voltage | Coil resistance (Ω) (at 23℃) | Operate voltage (at 23℃) | release voltage (at 23℃) | Allowable voltage range (at 23℃) | Nominal coil power (approx. W) |
|  |  | % of rated voltage |  |
| 003 | 11×(1±10%) | 80% max. | 5%min. | 95%-110% | 0.8 |
| 005 | 31×(1±10%) |  |  |  | 0.8 |
| 006 | 45×(1±10%) |  |  |  | 0.8 |
| 009 | 100×(1±10%) |  |  |  | 0.8 |
| 012 | 180×(1±10%) |  |  |  | 0.8 |
| 015 | 280×(1±10%) |  |  |  | 0.8 |
| 018 | 405×(1±10) |  |  |  | 0.8 |
| 024 | 720×(1±10%) |  |  |  | 0.8 |
| 036 | 1620×(1±10%) |  |  |  | 0.8 |
| 048 | 2880×(1±10%) |  |  |  | 0.8 |
| 060 | 4500×(1±10%) |  |  |  | 0.8 |
| 110 | 15125×(1±10%) |  |  |  | 0.8 |

| Coil data (DC spec:1.4W) |
| --- |
| Rated voltage | Coil resistance (Ω) (at 23℃) | Operate voltage (at 23℃) | release voltage (at 23℃) | Allowable voltage range (at 23℃) | Nominal coil power (approx. W) |
|  |  | % of rated voltage |  |
| 003 | 6×(1±10%) | 80% max. | 5%min. | 90%-110% (holding-voltage at 85℃ : 45%-90%) | 1.4 |
| 005 | 17×(1±10%) |  |  |  | 1.4 |
| 006 | 24×(1±10%) |  |  |  | 1.4 |
| 009 | 57×(1±10%) |  |  |  | 1.4 |
| 012 | 100×(1±10%) |  |  |  | 1.4 |
| 015 | 160×(1±10%) |  |  |  | 1.4 |
| 018 | 230×(1±10%) |  |  |  | 1.4 |
| 024 | 410×(1±10%) |  |  |  | 1.4 |
| 036 | 925×(1±10%) |  |  |  | 1.4 |
| 048 | 1645×(1±10%) |  |  |  | 1.4 |
| 060 | 2570×(1±10%) |  |  |  | 1.4 |
| 110 | 8068×(1±10%) |  |  |  | 1.4 |

| Coil data (DC spec:1.8W) |
| --- |
| Rated voltage | Coil resistance (Ω) (at 23℃) | Operate voltage (at 23℃) | release voltage (at 23℃) | Allowable voltage range (at 23℃) | Nominal coil power (approx. W) |
|  |  | % of rated voltage |  |
| 003 | 5×(1±10%) | 80% max. | 5%min. | 90%-110% (holding-voltage at 85℃ : 45%-70% ) | 1.8 |
| 005 | 13.5×(1±10%) |  |  |  | 1.8 |
| 006 | 20×(1±10%) |  |  |  | 1.8 |
| 009 | 45×(1±10%) |  |  |  | 1.8 |
| 012 | 80×(1±10%) |  |  |  | 1.8 |
| 015 | 125×(1±10%) |  |  |  | 1.8 |
| 018 | 180×(1±10%) |  |  |  | 1.8 |
| 024 | 320×(1±10%) |  |  |  | 1.8 |
| 036 | 720×(1±10%) |  |  |  | 1.8 |
| 048 | 1280×(1±10%) |  |  |  | 1.8 |
| 060 | 2000×(1±10%) |  |  |  | 1.8 |
| 110 | 6720×(1±10%) |  |  |  | 1.8 |

Ordering information

Note(1):

there are two specifications to W types: 1.5mm contact gap and 2.0mm contact .the default W type is 1.5mm type. if you want to use 2.0mm gap, please add the special code (456) when releasing order.

Note(2):

Coil power reference

|  | Normal gap DC type | Normal gap AC type | 1.5mm gap DC type | 2.0mm gap DC type |
| --- | --- | --- | --- | --- |
| Super Sensitivity | 0.2W (only for 2 form A type) | NON | NON | NON |
| sensitivity | 0.53W | 1.1-1.3VA | 0.8W | 1.4W |
| standard | 0.8W | NON | 1.4W | 1.8W |

Outline dimensions

1:  2A TYPE (12A TYPE) OUTLINE

2:  2C TYPE (12A TYPE) OUTLINE

3:  2B TYPE (12A TYPE) OUTLINE

4:  2A TYPE (16A TYPE) OUTLINE

5:  2C TYPE (16A TYPE) OUTLINE

6:  2B TYPE (16A TYPE) OUTLINE

# Text boxes

#### HL42K