| HANDOUK | SG RELAY |
| --- | --- |
|  | Features Input: DC control Double SCR AC output or TRIAC AC output 4000V dielectric strength Printed circuit board mount Environmental friendly product (RoHS compliant) |

INPUT (TA = 25 ℃)

| Input voltage | D | 3 to 32VDC |
| --- | --- | --- |
|  | 1D | 3 to 15VDC |
|  | 2D | 15 to 32VDC |
| Must operate voltage | D | 3VDC |
|  | 1D | 3VDC |
|  | 2D | 15VDC |
| Must release voltage | 1.0VDC |
| Max. Input current | D | 25mA |
|  | 1D | 40mA |
|  | 2D | 20mA |

OUTPUT (TA = 25℃ )

| Load voltage range | 48 to 280VAC (240VAC rated voltage) |
| --- | --- |
|  | 48 to 440VAC (380VAC rated voltage) |
|  | 48 to 530VAC (480VAC rated voltage) |
| Load current range | 0.1 to 5A |
| Max.surge current (10ms) | Triac output: 120Apk SCR output: 250Apk |
| Max.off-state leakage current | 1.5mA |
| Max.on-state voltage drop | 1.5Vrms |
| Max. turn-on time | Zero-cross | 1/2 cycle + 1ms |
|  | Random | 1ms |
| Max. turn-off time | 1/2 cycle + 1ms |
| Max. transient overvoltage | 600Vpk (at 240VAC rated voltage) |
| Min. off-state dv/dt | 800Vpk (at 380VAC rated voltage) |
|  | 1200Vpk (at 480VAC rated voltage) |
|  | 200V/μs |
| Min. power factor | 0.5 |
| Max. I2 t (10ms) | Triac output: 78A2 s SCR output: 310A2 s |

DESCRIPTION

SG pin-out  is compatible with standard OAC type I/O modules,

and all models are available with random turn-on as an alternative

to zero-cross turn-on.The SG SSR range offers a choice of

240VAC, 380VAC, 480VAC versions. Input Voltage specifications

have 3 to 15VDC, 15 to 32VDC and 3 to 32VDC.

PRECAUTIONS

- Soldering must be completed within 10 seconds at 260

or less or within 5 seconds at 350 or less.

2． The SSR case serves to dissipate heat. Install the relays

so that they are adequately ventilated. If poor ventilation is

unavoidable, reduce the load current by half.

3． The input circuitry does not incorporate a circuit protecting

the SSR from being damaged due to a reversed connection.

Make sure that the polarity is correct when connecting the

input lines.

4． When using the SG series for an AC load with a peak

voltage of more than the rated, connect the load terminals

of the relay to an inrush absorber (varistor). For 220VAC

the recommended varistor voltage is 470V; For 380VAC,

the recommended varistor voltage is 750V.

ORDERING INFORMATION

|  | SG | 2 | D- | 240 | A | 5 | Z | S- | N | G | (XXX) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Type |  |  |  |  |  |  |  |  |  |  |  |
| Input voltage | D:3 to 32VDC 1D:3 to 15V 2D:15 to 32V |  |  |  |  |  |  |  |  |  |
| Input voltage form | D: DC |  |  |  |  |  |  |  |  |
| Load voltage | 240: 240V 380:380V 480:480V |  |  |  |  |  |  |  |  |
| Load voltage form | A:AC |  |  |  |  |  |  |  |
| Load current | 3:3A 4:4A 5:5A |  |  |  |  |  |  |
| Zero cross function | Z: Zero cross turn-on P: Random cross turn-on |  |  |  |  |  |
| Output component | S: SCR Nil: TRIAC |  |  |  |  |
| RC snubber | N: Without RC snubber Nil: With RC snubber |  |  |  |
| Sead form | G: Epoxy resin dipped version Nil: plastic case version |  |  |
| Customer special code |  |

Notes: 1) If input voltage is D type(3-32VDC), the load voltage would be only available in 240V or 380V, and the output component is Triac only.

CHARACTERISTIC CURVES

Max. Load Current vs. Ambient Temp.                   Max. Permissible Non-repetitive Peak Surge Current vs. Number of Cycles(SCR AC switch output)

Ambient Temperature(℃)                      Number of cycles(at 50Hz)

Max. Pernissble Non-repetitive Peak Surge Current vs.Number of Cycles(TRIAC switch output)

Number of cycles(at 50Hz)

OUTLINE DIMENSIONS, WIRING DIAGRAM AND PC BOARD LAYOUT   Unit mm

OUTINE DIMENSIONS, WIRING DIAGRAM AND PC BOARD LATOUT    Unit mm